NATIONAL AGRI-FOOD BIOTECHNOLOGY INSTITUTE

- (Department of Biotechnology, Ministry of Science and Technology, Govt. of India)

- C-127, Industrial Area, Phase 8, SAS Nagar, Mohali, Punjab, India - 160071

- Phone: 0172-2290300 Fax: 0172-4604888

- Open Tender Notice No. NABI/2 (50)/10-11/N-PUR

(To be opened on 28th March, 2011)

- Executive Director, NABI invites tenders (Two Bid System) in closed/sealed covers with wax/cello tape/ company seal from the reputed Indian/foreign manufacturers or sole authorized dealers/distributors for the supply of the following item(s):

| Sr. No. | Tender No | Item Description | Qty | EMD (in Rs.) |
| --- | --- | --- | --- | --- |
| 1. | Tender No.NABI/2(50)/10-11/N-PUR | Online UPS 60KVA (Supply, Erection, Testing and commissioning of Double Conversion ONLINE UPS with in-built double wound isolating transformer, three phase 4 wire true sine wave output and sealed maintenance free batteries for 30 minutes backup to be erected in redundant mode. Complete with all accessories. Note: The erection cost of UPS shall include 160 4P MCBs in an enclosure on the incomer & 160A 4P isolator on outgoing side UPS to be suitable for unbalanced single phase loads on output side.. (Makes: APC, Emerson Liebert, Gutor/ Mitsubishi) | 3 No. | 80,000/- |

Interested parties may purchase the tender document directly from the office of NABI by paying Rs.300/- or download the tender documents directly from the website and attach a DD of Rs.300/- (Three Hundred only) in favour of National Agri-Food Biotechnology Institute as cost of tender documents.  Both the bids i.e. the Technical & Price bids must be submitted on or before 28th March, 2011 till 12:30 PM along with EMD.

The technical bid will be opened on 28th March, 2011 at 4:30 PM onwards in the presence of the bidders, who wish to be present.  The financial bid of only those tenderers who are assessed as technically qualified by the committee will be opened with prior intimation to the tenderer.

Date of Pre- Bid Conference:  On 18th March, 2011 at 12:30 PM at Board Room, NABI, Mohali.

Change in the technical specifications and terms & conditions if any, for the above item after pre-bid, will be posted on the NABI website.  All venders are requested to quote accordingly.

The Executive Director, NABI reserves the right to accept/reject any offer in part or full without assigning any reason.

STORES & PURCHASE OFFICER

NATIONAL AGRI-FOOD BIOTECHNOLOGY INSTITUTE

( (Department of Biotechnology Ministry of Science and Technology, Govt. of India)

C-127, Industrial Area, Phage 8, SAS Nagar, Mohali, Punjab

Phone: 0172-2290300 Fax: 0172-4604888

Open Tender Notice No: NABI/2 (50)/10-11/N-PUR

To be opened on 28th March, 2011 at 4:30 PM

Executive Director, NABI invites tenders from reputed Indian/foreign manufacturers and authorized dealers for SITC of the following item(s) under two bid systems:

| S.no. | Tender No. | Item Description | Qty | EMD (in Rs.) |
| --- | --- | --- | --- | --- |
| 1. | Tender No.: NABI/2 (50)/10-11/N-PUR | Online UPS 60KVA | 03 No | 80,000/- |

Note: SUPPLIERS WHO HAVE DOWNLOADED THE TENDER DOCUMENTS FROM THE WEBSITE, ARE REQUIRED TO ATTACH DEMAND DRAFT/PAY ORDER FOR Rs.300/- (THREE HUNDRED ONLY) FAVOURING NATIONAL AGRI-FOOD BIOTECHNOLOGY INSTITUTE, MOHALI, BEING THE COST OF TENDER DOCUMENTS, FAILING WHICH THE TENDER WILL NOT BE CONSIDERED.

Details of Demand Draft/Pay Order

- Demand Draft/Pay Order for Rs. 300/- (Rupees three hundred Only) drawn on _______________________________________________________________________________ is enclosed with technical bid towards the cost of tender documents

- Demand Draft/Pay Order for Rs.________________(Rupees____________________________

_____________________________________________ drawn on _______________________

___________________is enclosed with technical bid of the tender documents towards Earnest Money Deposit (EMD)

The detailed Tender Documents with complete terms & conditions with technical specifications are available on our website http://www.nabi.res.in

Date of Pre- Bid Conference:  On 18th March, 2011 at 12:30 PM at Board Room, NABI, Mohali.

Change in the technical specifications and terms & conditions if any, for the above item after pre-bid, will be posted on the NABI website.  All venders are requested to quote accordingly.

Last date of receipt of complete tenders is 28th March, 2011 till 12:30 PM

The date of opening of technical bids is 28th March, 2011 at 4:30 PM

Stores & Purchase Officer

NATIONAL AGRI-FOOD BIOTECHNOLOGY INSTITUTE

- (Department of Biotechnology Ministry of Science and Technology, Govt. of India)

- C-127, Industrial Area, Phage 8, SAS Nagar, Mohali, Punjab

# Phone: 0172-2290300 Fax: 0172-4604888

## Open Tender Notice No. NABI/2 (50)/10-11/N-PUR

To be opened on 28th March, 2011 at 4:30 PM

## Executive Director, NABI invites tenders (Two Bid System) in closed/sealed covers with wax/cello tape/ company seal from the reputed Indian/foreign manufacturers or sole authorized dealers/distributors for the supply of the following item(s):

| S.no. | Tender No | Item Description | Qty | EMD (in Rs.) |
| --- | --- | --- | --- | --- |
| 1 | NABI/2(50)/10-11/N-PUR | Online UPS 60KVA (Supply, Erection, Testing and commissioning of Double Conversion ONLINE UPS with in-built double wound isolating transformer, three phase 4 wire true sine wave output and sealed maintenance free batteries for 30 minutes backup to be erected in redundant mode. Complete with all accessories. Note: The erection cost of UPS shall include 160 4P MCBs in an enclosure on the incomer & 160A 4P isolator on outgoing side UPS to be suitable for unbalanced single phase loads on output side.. (Makes: APC, Emerson Liebert, Gutor/ Mitsubishi) | 3 No. | 80,000/- |

Interested parties may purchase the tender document directly from the office of NABI by paying Rs.300/- or download the tender documents directly from the website and attach a DD of Rs.300 (Three Hundred only) in favour of National Agri-Food Biotechnology Institute as cost of tender documents.  Both the bids i.e. the Technical & Price bids must be submitted on or before 28th March, 2011 till 12:30 PM along with EMD.

The technical bid will be opened on 28th March, 2011 at 4:30 PM onwards in the presence of the bidders, who wish to be present.  The financial bid of only those tenderers who are assessed as technically qualified by the committee will be opened with prior intimation to the tenderer.

Date of Pre- Bid Conference:  On 18th March at 12:30 PM at Board Room, NABI, Mohali.

Change in the technical specifications and terms & conditions if any, for the above item after pre-bid, will be posted on the NABI website.  All venders are requested to quote accordingly.

The Executive Director, NABI reserves the right to accept/reject any offer in part or full without assigning any reason.

*TB – Two Bid Tender System

STORES & PURCHASE OFFICER

# Technical specifications

Online UPS 60KVA  (Qty – 3 Nos.)

| TECHNICAL SPECIFICATION 60 KVA UPS WITH BUILT IN ISOLATION TRANSFORMER (THREE PHASE INPUT THREE PHASE OUTPUT) |  |  |
| --- | --- | --- |
| Sr. No. | Details | Specification |
| 1 | UPS technology | IGBT PWM Inverter , microprocessor controlled,Double conversion with digital display |
| 2 | Capacity | 60kva*3nos Parallel Redundant |
| 3 | Back up time at full load | 30 min on each UPS |
| 4 | Input Voltage (from no load to full load) & Frequency | 415± 15%v, 50HZ ± 5% |
| 5 | Output Voltage (from no load to full load) Frequency, Total harmonic distortion (Voltage) | 415 v ± 1%, 50 ± 0.05hz (Unsynchrosid) < 2.5% on linear load,< 5% on non linear load |
| 6 | Over all efficiency(double conversion mode) with isolation TRX IN-LINE | More than 92% |
| 7 | Over load capacity at 0.8pf | 110% for 60 min, 125% for 10 min, 150% for 1 min |
| 8 | Battery testing | Automatic battery testing |
| 9 | Static switch | Built in maintenance by pass & static switch with 100% rating |
| 10 | Manual Maintenance Bypass as Standard | Must be provided as Standard feature within UPS Cabinet |
| 11 | Parallel redundant | Parallel redundant provision up to 6 machines |
| 12 | Display | LCD display |
| 13 | Acoustic noise at rated load(at 1 mtr) | Less than 65 DBA |
| 14 | Isolation transformer | Inbuilt double wound K rated isolation transformer |
| 15 | Rectifier rating | 125 to 135% Inverter Capacity |
| 16 | Battery Bank shall have MCCB with UV &OV release contacts | Battery circuit Breaker of 160Amps for each UPS |
| 17 | Rectifier DC ripple | <1% with out battery connected |
| 18 | Maximum permissible non linear load | 100% with 3:1 crest factor |
| 19 | Transient Response | Output Voltage dip=+/-5%(0 to 100% load change & vice versa |
|  |  | Recovery time=less than 20m sec |
| 20 | Environmental characteristics | 0-40 degree C, 90% RH |
| 21 | Following protection shall be provided | A) overload and short circuit at out put of UPS |
|  |  | B) over voltage at output |
|  |  | C) deep discharge at battery terminals |
| 22 | Parameters available on LCD for the | a)Voltage:Output,bypass |
|  | following shall be provide:- | b) Output Current per phase |
|  |  | c)Load % on each Phase |
|  |  | d)Battery Current,Voltage,Remaining time & Total Load Utilization |
|  |  | e) Load KVA & KW on Each Phase |
|  |  | f) Output & Bypass frequency |
| 23 | Minimum VAH rating of battery bank for 30 min back up | 40,800 VAH |
| 24 | UPS shall be suitable to supply output power and charging current at the same time |  |
| 25 | Enclosures of UPS shall meet IP20 protaction requirements |  |
| 26 | UPS shall be provided with M.S battery Rack, Uninyvin Cable:battery to batteries & Battery bank to UPS, comprising of SMF Batteries VRLA type of the following make: Rocket/ Exide/ Amron |  |
| 27 | The erection cost of UPS shall include 160 4P MCBs in an enclosure on the incomer & 160A 4P isolator on outgoing side to be suitable for unbalanced single phase loads on output side.. (Makes: APC, Emerson Liebert, Gutor/ Mitsubishi) |  |

Bidder should give compliance statement point wise showing/highlighting items part no/serial number as quoted in their quotation for comprehensive technical comparison. Proof of compliance should be mentioned point wise in the catalogue.

Failing in compliance and proof of compliance will cause cancellation of the bid without any further notice/information.

Multiple Models with higher specifications should be quoted as separate models in the bids.

Open Notice No.-NABI/2(50)/10-11/N-Pur

TENDER DOCUMENT FOR OPEN TENDER

(TERMS & CONDITIONS INCLUDING INSTRUCTION TO BIDDERS AND CONDITIONS OF CONTRACT)

- GENERAL:  	Quotations in closed cover are invited on behalf of the Executive Director, National Agri-Food Biotechnology Institute, Mohali from the reputed Indian and foreign manufacturer. The offer/ quotation must be strictly as per required specifications and the tender terms & conditions.

- PREPARATION AND SUBMISSION OF OFFERS:

- Quotation should be submitted directly by the original manufacturer/supplier or its sole authorized distributor/dealer. In case of bid by authorized dealer/distributor, the manufacturer authorization should be attached with the technical bid as per Annexure-‘F’.

- In case a bidder is not doing business within India, it shall furnish the certificate to the effect that the bidder is or will be represented by an agent in India equipped and able to carry out the supply, maintenance, repair obligations etc. during the warranty and post-warranty period or ensure a mechanism at place for carrying out the supply, maintenance, repair obligations etc. during the warranty and post-warranty period.

- The bidder shall bear all costs associated with the preparation and submission of its bid irrespective of the conduct or outcome of the bidding process.

- The bidder should not indulge in any corrupt, fraudulent, collusive, coercive practices during the entire process of procurement and execution of contract/order.

- Before the deadline for submission of the bid, NABI reserves the right to modify the bidding document and to extend or not to extend the date of submission. Such amendment/modification will be notified to bidders receiving the bidding document in writing or by cable/fax/ email and will also be hosted on NABI website.

- Conditional tenders will be summarily rejected.

- A bidder may withdraw, substitute, or modify its bid after it has been submitted by sending a written notice signed by the authorized signatory before the date of submission of the bid. Any re-submission or modification in the bid should be submitted before the date & time of submission of bid as originally conveyed in the invitation of bid.

- No bid may be withdrawn, substituted or modified in the interval between the deadline for submission of bids and the expiration of the period of bid validity specified by the Bidder on the Bid Form or any extension thereof.

- First envelope marked “WITHDRAWAL” shall not be opened, but returned to the Bidder subject to submission of valid authorization to request the withdrawal. In case of substituted and modified bid, only the substituted bids and modified bids will be opened subject to production of authorization from the bidders.

- The quotation should be addressed to the Executive Director, NATIONAL AGRI-FOOD BIOTECHNOLOGY INSTITUTE, Mohali and sent to the Stores & Purchase Officer.

- Each offer/quotation should be kept in separate envelope against each item of the tender notice.

- For items covered under Two-Bid -Tender System, quotation/offer should be submitted in two separate envelopes containing Techno-Commercial bid and Price bid and these put in one envelope.

- The outer cover containing the offer/quote should be super-scribed with our Tender No. (Not global/open Tender Notice No), Due date and Date of opening of tender.

- The offers must contain the following documents :-

- Techno-commercial offers must contain:

      - Manufacturer authorization (as per clause 2(a)) as per Annexure –‘E’.

      - Certificate by bidder not doing business in India as per clause 2(b).

      - Technical literature/ leaflets and complete specifications of quoted model(s) along with commercial terms and conditions.

      - Compliance statement/questionnaire of tender terms and conditions as per Annexure-‘A’

      - Compliance statement of specifications as per Annexure- ‘B’

      - Integrity Pact- Only in case of bids of more than Rs. 3.00 Crore (as per Annexure- ‘C’)

      - Copies of previous supply orders (as per clause 10(c) and clause 25) as per Annexure –‘G’.

      - Details of supplies of similar equipments as per clause 10(d).

- Price Bid offers must contain: (Only in case of two bid system)

i.	Bid price as per clause 5 in format enclosed as Annexure- ‘D’ or Annexure- ‘E’ as applicable.

ii.	Certificate of price reasonability as per clause 10(b).

- DUE & OPENING DATES:     The Offer/Quotations must reach at NABI as mentioned above on page No.1 in the presence of bidders, who wish to present themselves at the time of opening of tender. In case opening date happens to be a holiday, the tender will be opened on next working day at the same time & location. The price bids of two bid tender system shall be opened after technical evaluation of technical bids. The date of opening of price bids shall be informed to the bidders found suitable in technical evaluation. No request for extension in the date of submission & opening of tender will be entertained. However NABI, may at its discretion, extend the deadline for submission of bids under intimation to bidders.

.

- PRICES

Bid prices should be filled in the appropriate format enclosed as Annexure ‘D’ and ‘E’.

- For goods manufactured with India:

- The price of goods quoted Ex-Works including taxes already paid.

- VAT and other taxes like excise duty etc. which will be payable on the goods if the contract is awarded.

- The charges for inland transportation, insurance and other local service required for delivering the goods at the desired destination as specified in the price schedule form.

- The installation, commissioning and training charges including any incidental services, if any.

- For goods manufactured abroad:

- The price of the goods, quoted on FCA(including inland freight) (Named place of delivery abroad) or FOB (Named port of shipment), as specified in the schedule form.

- The charges for insurance and transportation of the goods to the port/place of destination.

- The agency commission charges, if any.

- The installation, commissioning and training charges including any incidental services, if any.

- We are exempted from payment of Excise Duty under notification number 10/97 dated 01.03.1997and Customs Duty under notification No.51/96 dated 23.07.1996.  Hence Excise Duty and Customs Duty, if any, should be shown separately.   No other charges than those mentioned clearly in the quotation will be paid.

- Sales Tax: We are not authorized to issue any Sales Tax Form ‘C’ & ‘D’.

- VALIDITY OF OFFER :

The prices must be valid at least for a period of 90 days for indigenous supplies & 180 days for imports from the date of opening of the Tender.  No changes in prices will be acceptable in any condition after opening of tender till the validity of the offer or execution of the order whichever is later.

- EVALUATION OF BIDS: 	Before submission of bid, the bidder is expected to examine all the instructions, forms, terms and specifications in the bidding document and should ensure that the following conditions are fulfilled:

  - Bidder Information form as per Annexure-‘H’.

  - The price schedule should be enclosed and must be signed.

  - The bid validity should not be shorter than required.

  - The manufacturer’s authorization should be enclosed in case the bidder is authorized dealer/ distributor.

  - The bidders should agree to provide the Performance Security.

  - The quoted goods should be as per required specifications.

  - In case the bid is substantially responsive, the purchase may request that bidder may submit the necessary information, documentations, within a reasonable period of time, to rectify, non-material, non-conformities or omission in the bid related to documentation requirements. Failure of the bidders to comply with the request may result in the rejection of its bids. But in case of the material deviation/reservation or omission which limits or is inconsistent with the bidding documents and the Purchaser’s Rights or Bidders obligation under the contract or which if rectified, would unfairly affect the other bidders, the bid will be rejected.

  - The Purchaser shall correct arithmetical errors on the following basis:

- If there is a discrepancy between the unit price and the line item total that is obtained by multiplying the unit price by the quantity, the unit price shall prevail and the line item total shall be corrected, unless in the opinion of the Purchaser there is an obvious misplacement of the decimal point in the unit price, in which case the line item total as quoted shall govern and the unit price shall be corrected.

- If there is an error in a total corresponding to the addition or subtraction of  subtotals, the subtotals shall prevail and the total shall be corrected; and

- If there is a discrepancy between words & figures, the amount in words shall prevail, unless the amount expressed in words is related to an arithmetic error, in which case the amount in figures shall prevail subject to (i) and (ii) above.

  - Selling exchange rate/equivalent to Indian currency will be as on the date of bid opening in the case of single bidding and the rate on the date of opening of the priced bids in the case of two-part bidding.

  - The bids shall be evaluated on the basis of final landing cost as per Annexure –‘D’ in case of import and Annexure –‘E’ in case of indigenous items.

  - The comparison between the indigenous and the foreign offers shall be made on FOR destination basis and CIF/CIP basis respectively. However the CIF/CIP prices quoted by any foreign bidders shall be loaded further as under :

- Towards customs duty and other statutory levies-as per applicable rates.

- Towards custom clearance, inland transportation etc. – 2% of the CIF/CIP value.

  - Where the price quoted on FOB/FCA and CIF/CIP basis are the same, the Contract would be made on CIF/CIP basis only.

  - The Purchaser reserves the right at the time of Contract award to increase or decrease the quantity of goods and services originally specified in the tender document without any change in unit price or other terms and conditions. Further, at the discretion of the purchaser, the quantities in the contract may be enhanced by 30% within the delivery period.

- The Vague terms like “packing, forwarding, transportation………….. etc. extra” without mentioning the   specific amount/percentage of these charges will not be accepted.  Such offers shall be treated as incomplete and rejected.

- INTEGRITY PACT: 	In case of purchases valuing more than Rs. 3 crore, it in mandatory for the supplier(s) to enter into an Integrity Pact with NABI as per the proforma enclosed as Annexure –‘C’, failing which their bid will not be considered.

- REASONABILITY  OF PRICES :

  - Please quote best minimum prices applicable for a premier Research Institution, leaving no scope for any further negotiations on prices.

  - The quoting party should give a certificate to the effect that the quoted prices are the minimum and they have not quoted the same item on lesser rates than those being offered to NABI to any other customer nor they will do so till the validity of offer or execution of the purchase order, which ever is later.

  - Copies of at least last three supply orders of the last 3 years received from other customers along with details of such supply orders preferably in India for the same item/model may be submitted with the offer giving reasons of price difference of their supply order & those quoted to us, if any. (As per Annexure –‘G’).

  - The party must give details of identical or similar equipment, if any, supplied to any CSIR lab during last three years along with the final price paid and Performance certificate from them.

- ANNUAL MAINTENANCE CHARGES:  	The party must mention in the quotation, the rate/amount of annual maintenance charges, if we opt for maintenance contract after expiry of the warranty period.  This is mandatory to mention.

- SPECIFICATIONS:

A. 	Specifications are basic essence of the product.  It must be ensured that the offers must be strictly as per our specifications. At the same time it must be kept in mind that merely copying our specifications in the quotation shall not make the parties eligible for consideration of the quotation.  A quotation has to be supported with the printed technical leaflet/literature of the quoted model of the item by the quoting party/manufacturer and the specifications mentioned in the quotation must be reflected/ supported by the printed technical leaflet/literature. Therefore the model quoted invariably be highlighted in the leaflet/literature enclosed with the quotation. Non-compliance of the above shall be treated as incomplete/ambiguous and the offer can be ignored without giving an opportunity for clarification/negotiation etc. to the quoting party

B.	The technical bid shall be evaluated for acceptability by the technical committee and may call the tenderers for discussion. If necessary, the committee may modify the technical specification to suit the NABI requirement.

- COMPLIANCE STATEMENTS:

a. 	Bidders must furnish a Compliance Statement of each and every required Specification of our tender in the format at ANNEXURE –‘B’.  The deviations, if any, from the tendered specifications should be clearly brought out in the statement. Technical literature/leaflet showing the compliance of the specification may also be attached with the quotation.

b. 	Similarly, the Compliance Statement/questionnaire for Terms & Conditions of the tender may be furnished, as per the enclosed format at Annexure –‘A’, along with quotation (with techno- commercial bid in case of two bid tender system).

c.  	The firms are advised to submit both the compliance statements essentially along with their quotation failing which their offer may not be considered.

- PERIOD & MODE OF DELIVERY:  	The delivery period is the essence of supply; hence it must be indicated specifically in the quotation.   Mode of delivery, tentative size and weight of consignment may also be indicated in the quotation.

- PERFORMANCE SECURITY: 	All the successful bidders will have to submit the Performance Bank Guarantee or establish a Standby Letter of Credit (SLOC) or a Bankers cheque / or FDR pledged in favour of EXECUTIVE DIRECTOR, NABI for required amount as per payment terms mentioned at clause 16 below except where supplier opts for release of amount equivalent to PBG after expiry of warranty period.  The PBG format shall be provided to the successful bidder later on along with the purchase order.

- PAYMENT CONDITION:

A.   FOR INDIGENEOUS SUPPLIES:

Payment on Bill Basis after supply:  For local supplies the payment will be made only after satisfactory installation, commissioning and performance of the equipment at NATIONAL AGRI-FOOD BIOTECHNOLOGY INSTITUTE, MOHALI and after certification by our technical expert/scientist.  However, supplier will be required either to submit performance bank guarantee for 10% amount of the total value of equipment, after installation of the material, valid up to 60 days after the expiry of warranty period or the equivalent amount shall be released after expiry of the satisfactory warranty period.

B.   FOR IMPORTS:

The payment against imports shall be made through irrevocable L/C. L/C will be opened for 100% FOB/CIF value. 100% of L/C amount shall be released on presentation of complete and clear shipping documents, subject to submission of PBG of equivalent amount to cover the warranty period. The PBG should remain valid up to 60 days after the expiry of warranty period. In case of non-submission of PBG after installations/demonstration/commissioning, remaining payment i.e. 10% will be released only after the completion of warranty period.

- COMMENCEMENT OF WARRANTY PERIOD: 	The warranty period of an item shall commence from the date of receipt of the item in good working condition and satisfactory installation/commissioning/demonstration at the project site in NATIONAL AGRI-FOOD BIOTECHNOLOGY INSTITUTE, MOHALI.  The warranty period and validity of Performance Guarantee shall be extended for the period of delay in satisfactory installation and delay in warranty services.

- NO ADVANCE PAYMENT: No advance payment will be made to any supplier.

- INSTALLATION:	 The equipment should be installed/commissioned and demonstrated, by the supplier at the lab immediately but in any case within one month after receipt of the item in the lab and the same will be put under operation to the satisfaction of our technical expert/Scientist who will test the performance of the equipment.   No separate charges for installation etc. will be paid to the party beyond the quoted prices.

- GUARANTEE/WARANTY:  The equipment/instrument (including batteries) must be guaranteed/ warranted for a period of at two year, if not specifically mentioned otherwise in the specifications sheet, from the date of its satisfactory installation/commissioning against all manufacturing defects.  If the equipment is found defective during this period the whole equipment or part thereof will have to be replaced/ repaired by the supplier free of cost at the lab. or at site of the supplier for which ‘to and fro’ expenses will be borne by the supplier.   However, if   the items are guaranteed for a period of more than one year, it may be specifically mentioned in the quotation.

- SPARE PARTS:  	Availability of spare parts of the equipment/instrument must be guaranteed for a period of at least five years from the date of supply.

- AFTER SALES SERVICES:  It should be clearly mentioned in the quotation whether the after sales services during and after the completion of warranty shall be provided directly by the supplier or their authorized agent/representative.  Cost of AMC and CMC should be mentioned in the price bid for (05) five years after the elapse of warranty period.  However, in both the cases the original supplier shall be responsible for poor performance/services.  The company should have service engineers within 300 km of the range of the institute.

- INSPECTION :

- The inspection of the system will be done by our technical expert /Scientist in the presence of firm’s representative.

- In case of receipt of the material in short supply or damaged condition the supplier will have to arrange the supplies/ replacement of goods free of cost pending the settlement of the insurance case wherever applicable on FOR at the lab.  or CIF basis till satisfactory installation of the system.

- The supplier should arrange for physical Inspection of the items directly or through their authorized representative within seven days of arrival of the consignment failing which they will be responsible for the losses. After the shipment is effected, the supplier/its representative/Indian agents must remain in touch with the lab/instt. to ascertain the date of arrival of consignment.

- AUTHORIZATION OF INDIAN AGENTS & INDIAN REPRESENTATIVE:

- In case there is involvement of an /Indian agent/representative in any form as mentioned at (b) below, an authority letter / copy of agreement from the principal manufacturer must be submitted with the quotation.

- Where quoting party/Indian representative claims to be the subsidiary or branch office or an authorized representative of the principal foreign manufacturer/supplier in India, then a copy of approval from RBI/Ministry for operating business in India as Subsidiary/Branch/Liaison office or Joint-Venture may be submitted with offer.

- The details of all supplies involving the foreign exchange shall be furnished to the Enforcement Directorate, Chandigarh as per rule.  It may be noted that only the quoting parties & their principals shall be responsible for violation of Foreign Exchange Management Act (FEMA) for not declaring the actual bilateral mutual interests, if any.

- Indian agency commission shall be paid only to the Indian Agents in Indian Rupee out of the quoted FOB/Ex-works prices, after receipt of goods in good working condition & satisfactory installation/demonstration/commissioning of the items.

- USERS LIST :

a.	The list of users specifically for the same model/make of the quoted item (not the list of general users) along with the   complete name, address & contact numbers of the user organizations/persons may be submitted with the quotation along with the performance certificates from all/some of them.

b.	If you have supplied identical or similar equipment to other CSIR Labs./DBT Insts., the details of such supplies for the preceding three years shall be given together with the prices finally paid.

- PENALTY CLAUSE FOR LATE DELIVERY & LATE INSTALLATION:

- Subject to operation of Force Majeure, time for delivery and acceptance is the essence of this contract.  The supplier shall arrange to ship the ordered materials within the delivery period mentioned in the order unless extended with/without penalty.

- In case of delay in supply on part of the supplier, a penalty @ 1% per week of Order/FOB value will be charged for delayed period subject to a maximum of 10% of order/FOB value.

- If the delay in the shipment of the ordered materials attributable to the supplier exceeds agreed time period from the date of original agreed upon date of shipment and extended with/without penalty, the NATIONAL AGRI-FOOD BIOTECHNOLOGY INSTITUTE shall have the right to cancel the contract/purchase order and recover the liquidated damages from other dues of the party or by legal means. It will also affect the other/future business dealings with such suppliers.

- The same rate of penalty shall be applicable for late installation of the equipment/instrument also.

- TRAINING: 	Wherever needed, Our Technical person(s) should be trained by the supplier at the project site free of cost.  In case the person is to be trained at supplier’s site abroad or in India it should be mentioned in the quotation clearly.   The supplier should bear all the expenses for such training including ‘to & fro’ fares and lodging & boarding charges.

- NON-SUBMISSION OF TENDER: In case you are unable to submit your quotation against our tender enquiry we would appreciate and expect a note of regret from your side giving in brief, reasons for not quoting.

- DELETION OF NAME : Names of bidders,  backing-out/defaulting after opening of tenders will be recommended for deletion from the list of suppliers in addition to forfeiture of EMD submitted by them, if any.

- LATE/ DELAYED /UNSOLICITED QUOTATION: Late or delayed/Unsolicited quotations/offers shall not be considered at all. These will be returned to the firms as it is. Post tender revisions/corrections shall also not be considered.

- ACCEPTANCE OR REJECTION OF OFFER: The Executive Director, NATIONAL AGRI-FOOD BIOTECHNOLOGY INSTITUTE, MOHALI reserves the right to accept or reject any quotation /tender in part or full without assigning any reason thereof.  The successful bidder should submit Order acceptance within 15 days from the date of issue.

- PAGE NUMBERING & SIGNATURES:  Your offer should be a page numbered and signed by an authorized signatory giving his/her name and designation below the signatures.

- INTERIM ENQUIRIES:  No interim inquiries will be attended.

- FORCE MAJEURE:  The Supplier shall not be liable for forfeiture of its performance bank guarantee, liquidated damages or termination for default, if and to the extent that, it’s delay in performance or other failure to perform its obligations under the Contract is the result of an event of Force Majeure.  For purposes of this Clause, “Force Majeure” means an event beyond the control of the Supplier and not involving the Supplier’s fault or negligence and not foreseeable.  Such events may include, but are not limited to, acts of the Purchaser either in its sovereign or contractual capacity, wars or revolutions, fires, floods, epidemics, quarantine restrictions and freight embargoes.

If a Force Majeure situation arises, the Supplier shall promptly notify the Purchaser in writing of such conditions and the cause thereof.  Unless otherwise directed by the Purchaser in writing, the Supplier shall continue to perform its obligations under the contract as far as is reasonably practical, and shall seek all reasonable alternative means for performance not prevented by the Force Majeure event.

- DISPUTE SETTLEMENT: All disputes arising out of this contract shall be referred to the sole arbitration of the Executive Director of National Agri-Food Biotechnology Institute, Mohali or his nominee, who is overall controlling authority of this laboratory as per the provisions of Indian Arbitration and Reconciliation Act 1996 and his award shall be final and binding on the parties to the dispute.   However, in case of importers, the provisions related to Arbitration as per the United Nations Commission on International Trade Laws (UNCTRAL) will be applicable and binding on both the parties. The venue of arbitration in both the above cases will be Chandigarh (INDIA).

(Stores & Purchase Officer)

Encl:

      - Format for Compliance of Terms & Conditions.

      - Set of Specifications

Annexure -‘A’

FORMAT/QUESTIONNAIR FOR COMPLIANCE OF TERMS AND CONDITIONS

Tender No.: ______________________				                   Due Date __________________

NOTE:

- Quotation will not be considered without submission of this format.

- If a particular question is not at all applicable please write NA in compliance part in Col. No.  4 below.

- Kindly see the relevant terms & conditions of the tender document as mentioned in Col. No. 3 in each question before replying to the questions mentioned in Col. 2 below).

| SNo | Terms & condition of Tender document | Relevant Clause No. of the tender terms & conditions of the tender | Whether acceptable (say ‘Yes’ or ‘No’ (preferably use different colour ink for ‘No’) | Deviation from tender terms, if any, with reasons for noncompliance or alternative condition quoted for |
| --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 |
| 1 | a.) Whether quotation is direct from Principal supplier/manufacturer or their own office in India (Please specify) | Clause 2(a) |  |  |
|  | b) Whether quotation is being submitted by Indian Agent/authorized distributor/ dealer | Clause 2(a) |  |  |
|  | c) Whether the agent is registered with DGS&D/NSIC | Clause 4(a) |  |  |
| 2 | a) Whether the Techno-commercial and price bids (for two bid tender system only) have been kept in separate envelopes duly marked with “Techno-commercial Bid” and “Price Bids” respectively. | Clause 2(l) |  |  |
|  | b) Whether the tender No., Due date & Opening dates have been written outside all the envelopes. | Clause 2 (m) |  |  |
| 3 | Whether techno-commercial Bid contains EMD, technical literature/leaflets, detailed specifications & commercial terms & conditions etc. as applicable. | Clause 2(n)(A) |  |  |

| 4 | - If the prices are on Ex-Works basis or FOB (names port of shipment ) or FCA (named place of delivery abroad) | Clause 5 (A) & (B) |  |  |
| --- | --- | --- | --- | --- |
|  | - Whether specific amounts or percentage of expenses like packing, forwarding, handling, freight, insurance, documentation etc. have been mentioned in quotation separately in clear terms. | Clause 5(B), (C) & (D) |  |  |
| 5 | a) Whether prevailing rates of sales tax, excise duty & other govt. levies (for indigenous supplies) have been given in quotation | Clause 5 (A), (C) & (D) |  |  |
| 6 | Have you mentioned the validity period of the quotation as per our requirements | Clause 6 |  |  |
| 7 | a) Whether the Price reasonability Certificate is submitted with quotation | Clause 10 (b) |  |  |
|  | b) Whether copies of last two supply orders of the same item from other customers have been attached with the quotation | Clause 10 (c) |  |  |
|  | c) If there is any difference in prices of last two orders & those quoted to us. If yes, please give reasons for the same | Clause 10 (c) |  |  |
|  | d) Whether supplied in CSIR/DBT Labs. | Clause 10 (d) |  |  |
| 8 | Whether rates/amount of AMC after the warranty period is over has been mentioned | Clause 11 |  |  |
| 9 | Have you gone through the specification Clause & complied with the same | Clause 12 (A) & (B) |  |  |
| 10 | Whether the Make/Brand, Model number and name of manufacturer has been mentioned in the quotation and Printed technical literature/ leaflets of quoted items have been submitted |  |  |  |

| 11 | Whether compliance statement of specifications has been attached with the quotation. | Clause 13 (a) & annexure- ‘E’ |  |  |
| --- | --- | --- | --- | --- |
| 12 | a) Whether the delivery period for supply of the items has been mentioned | Clause 14 |  |  |
|  | b) Whether mode of delivery & tentative size & weight of the consignment has also been indicated | Clause 14 |  |  |
| 13 | Do you agree to the submission of Performance Bank Guarantee/Standby L/C and have you mentioned in your quotation about this. | Clause 13 |  |  |
| 14 | a) Do you agree with the payment terms for indigenous supplies? | Clause 16A |  | No deviation permitted |
|  | b) Do you agree with the payment terms for imports supplies? | Clause 16 B |  |  |
| 15 | Do you agree about the date of commencement of warranty period & its extension is necessary. | Clause 17 |  |  |
| 16 | a) Who will install/commission and demonstrate the equipment at lab. FREE OF COST | Clause 19 |  |  |
|  | b) Will you be able to do it within a month | Clause 19 |  |  |
| 17 | Have you mentioned the guarantee/warrantee period in your quotation and do you agree with guarantee clause? | Clause 20 |  |  |
| 18 | Spare parts | Clause 21 |  |  |
| 19 | After Sales service | Clause 22 |  |  |
| 20 | a) Do you agree that on receipt of material in damaged condition or short supply you will replace the same on CIF basis, free of cost pending the settlement of the insurance claim? | Clause 23 (b) |  |  |
|  | b) Do you agree with the clause of physical inspection? | Clause 23 (c) |  |  |
| 21 | For Import Cases only: a) Whether the Indian agent is registered with DGS&D | Clause 24 |  |  |
|  | b) Whether the valid DGS& D registration certificate has been enclosed with the offer | Clause 24 (b) |  |  |
|  | c) If the party is a subsidiary or corporate branch office of the foreign supplier, then whether copy of the approval from Reserve Bank of India is attached with the offer | Clause 24 (c) |  |  |

| 22 | Whether list of specific user’s for the same item & model as quoted along-with performance certificates from the users is submitted with offer | Clause 25 |  |  |
| --- | --- | --- | --- | --- |
| 23 | Whether you agree to the penalty clause for late delivery & installation? | Clause 26 (a to d) |  |  |
| 24 | Whether training to our technical person will be given free of cost. If yes, have you specified in quotation whether it will be in our lab? Or at supplier’s site in India or abroad. | Clause 27 |  |  |
| 25 | a) Whether all the pages have been page numbered? | Clause 32 |  |  |
|  | b) Whether quotation has been signed and designation & name of signatory mentioned. | Clause 32 |  |  |
| 26 | Do you agree to settle the issue through the sole arbitration of the Executive Director or his nominee? | Clause 35 |  |  |

Signatures of the authorized signatory_________________

Name of the signatory ______________________________

Designation ______________________________________

Name & Seal of the quoting party ___________________

Dated:___________

Annexure-‘B’

## FORMAT OF COMPLIANCE STATEMENT OF SPECIFICATIONS

| S. N. | Name of specifications/ part / Accessories of tender enquiry | Specifications of quoted Model/ Item | Compliance Whether “YES” Or “NO” | Deviation, if any, to be indicated in unambiguous terms | Whether the compliance / deviation is clearly mentioned in technical leaflet/ literature |
| --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 |

Annexure-‘C’

FORMAT OF THE INTEGRITY PACT

## Integrity Pact

## Between

## NATIONAL AGRI-FOOD BIOTECHNOLOGY INSTITUTE (NABI) hereinafter called to as “The Principal”

And

………………………………………………………………………..… hereinafter referred to as “The Bidder/Contractor”

Preamble

The Principal intends to award, under laid down organizational procedures, contract/s for ……………………………………. The Principal values full compliance with all relevant laws of the land, rules, regulations, economic use of resources and of fairness/transparency in its relations with its Bidder(s) and /or Contractor(s).

In order to achieve these goals, the Principal will appoint an Independent External Monitor (IEM), who will monitor the tender process and the execution of the contract for compliance with the principles mentioned above.

Section 1 – Commitments of the Principal

- The Principal commits itself to take all measures necessary to  prevent corruption and to observe the following principles:

        - No employee of the Principal, personally or through family members, will in connection with the tender for , or the execution of a contract, demand, take a promise for or accept, for self or third person, any material or immaterial benefit which the person is not legally entitles to.

        - The Principal will, during the tender process treat all Bidder(s) with equity and reason. The Principal will in particular, before and during the tender process, provide to all Bidder(s) the same information and will not provide to any Bidder(s) confidential/additional information through which the Bidder(s)confidential/ additional information through which the Bidder(s) could obtain an advantage in relation to the tender process or the contract execution.

        - The Principal will exclude from the process all known prejudiced persons.

- If the Principal obtains information on the conduct of any of its employees which is a criminal offence under the IPC/PC Act, or if there be a substantive suspicion in this regard, the Principal will inform the chief Vigilance Officer and  in addition can initiate disciplinary action.

Section 2 – Commitments of the Bidder(s) / Contractor(s)

- The Bidder(s) /Contractor(s) commit himself to take all measures necessary to prevent corruption. He commits himself to observe the following principles during his participation in the tender process and during the contract execution

              - The Bidder(s)/ Contractor(s) will not, directly or through any other person of form, offer, promise or give to any of the Principal’s employees involved in the tender process or the execution of the contract or to any third person any material or other benefit which he/she is not legally entitled to, in order to obtain in exchange any advantage of any kind whatsoever during the tender process or during the execution of the contract.

              - The Bidder(s)/ Contractor(s) will not enter with other Bidders into any undisclosed agreement or understanding, whether formal or informal. This applies in particular to prices, specifications, certifications, subsidiary contracts, submission or non-submission of bids or any other actions to restrict competitiveness or to introduce cartelization in the bidding process.

              - The Bidder(s)/ Contractor(s) will not commit any offence under the relevant IPC/PC Act; further the Bidder(s)/ Contractor(s) will not use improperly, for purposes of competition or personal gain, or pass on to others, any information or document provided by the Principal as part of the business relationship, regarding plans, technical proposals and business details, including information conta8ined or transmitted electronically.

              - The Bidder(s)/ Contractor(s) of foreign origin shall disclose the name and address of the agents/representatives in /India, if any. Similarly the Bidder(s)/ Contractor(s) of Indian Nationality shall furnish the name and address of the foreign principals, if any. Further details as mentioned in the “guidelines on Indian agents of Foreign Suppliers” shall be disclosed by the Bidder(s)/ Contractor(s). Further, as mentioned in the Guidelines all the payments made to the Indian Agent/representative have to be in Indian Rupees only. Copy of the “Guidelines on Indian Agents of Foreign Supplies” is annexed and marked an Annexure.

              - The Bidder(s)/ Contractor(s) will, when presenting his bid, disclose any and all payments he has made, is committed to or intends to make to agents, brokers or any other intermediaries in connection with the award of the contract.

- The Bidder(s)/ Contractor(s) will not instigate third persons to commit offences outlines above or be an accessory to such offences.

Section 3 – Disqualification from tender process and exclusion from future contracts

If the Bidders(s) / Contractor(s), before award or during execution has committed a transgression through a violation of Section2, above or in any other form such as to put his reliability or credibility in question, the Principal is entitled to disqualify the Bidders(s) / Contractor(s), from the tender process or take action as per the procedure mentioned in the “Guidelines on Banning of Business Dealing”. Copy of the “Guidelines on Banning of Business Dealing” is annexed and marked as Annex –“B”.

Section 4- Compensation for Damages

- If the Principal has disqualified the Bidder(s) from the tender process prior to the award according to Section 3, the Principal is entitles to demand and recover the damages equivalent to Earnest money Deposit/Bid Security.

- If the Principal has terminated the contract according to Section 3 or if the Principal is entitles to terminate the contract according to Section 3, the Principal shall be entitles to demand and recover from the Contractor liquidated damage of the contract value or the amount equivalent to Performance Bank Guarantee.\

Section 5 – Previous transgression

- The Bidder declares that no previous transgressions occurred in the last 3 years with any other company in any country conforming to the anti corruption approach or with any other Public Sector enterprises in India that could justify his exclusion from the tender process.

- If the Bidder makes incorrect statement on this subject, he can be disqualified from the tender process or action can be taken as per procedure mentioned in “Guidelines on Banning of business dealings.”

Section 6 – Equal treatment of all Bidders/ Contractors/ Sub Contractors

- The Bidder(s)/ Contractor(s) undertake(s) to demand from all sub contractors a commitment in conformity with this Integrity Pact, and to submit it to the Principal before contract signing.

- The Principal will enter into agreement with identical conditions as this one with all Bidders, Contractors and Sub contractors.

- The Principal will disqualify from the tender process all bidders who do not sign this Pact or violet its provisions.

Section 7 – Criminal charges against violating Bidders/ Contractors/ Sub Contractor

- The Principal appoints competent and credible Independent External monitor for this Pact. The task of the Monitor is to review independently and objectively, whether and to what extent the parties comply with the obligations under this agreement.

- The Monitor is not subject to instructions by the representatives of the parties and performs his functions neutrally and independently. He reports to the Executive Director, NABI.

- The Bidder(s)/ Contractor(s) accepts that the monitor has the right to access without restriction to all Project documentation of the Principal including that provided by the Contractor. The contractor will also grant the Monitor, upon his request and demonstration of a valid interest, unrestricted and unconditional access to his project documentation. The same is applicable to Subcontractors. The Monitor is under contractual obligation to treat the information and documents of the Bidder(s) Contractor(s)/ sub Contractor(s) with confidentiality.

- The Principal will provide to the Monitor sufficient information about all meetings among the parties related to the Project provided such meetings could have an impact on the contractual relations between the Principal and the Contractor. The parties offer to the Monitor the option to participate in such meetings.

- As soon as the Monitor notice, or believes to notice, a violation of this agreement, he will so inform the Management of the Principal and request the Management to discontinue or take corrective action, or to take other relevant action. The monitor

can in this regard submit non-binding recommendations. Beyond this, the Monitor can in this regard to demand from the parties that they act in a specific manner, refrain from action or tolerate action.

- The monitor will submit a written report to the Executive Director, NABI within 8 to 10 weeks from the date of reference or intimate to him by the Principal and should the occasion arise, submit proposals for correcting problematic situations.

- Monitor shall be entitled to compensate on the same terms as being extended to/provide to Independent Directors on the

NABI

- If the Monitor has reported to the Executive Director, NABI as substantiated suspicion of an offence under relevant IPC/PC Act, and the Executive Director, NABI has not, within the reasonable time taken visible action to proceed against such offence or reported it to the Chief Vigilance Officer, the Monitor may also transmit this information directly to the Central Vigilance Commissioner.

- The word ‘Monitor’ would include both singular and plural.

Section 8 – Pact Duration

This pact begins when both parties have legally signed it. It expires for the Contractor 10 months after the last payment under the contract, and for all other Bidders 6 months after the contract has been awarded.

If any claim is made/lodged during this time, the same shall be binding and continue to be valid despite the lapse of this pact as specified above, unless it is discharged/determined by Director, NABI.

Section 9 – Other provisions

- This agreement is subject to Indian Law, Place of performance and jurisdiction is the Registered Office of the Principal, i.e. Chandigarh.

- Changes and supplements as well as termination notices need to be made in writing. Side agreements have not been made.

- If the Contractor is a partnership or consortium, this agreement must be signed by all partners or consortium members.

- Should one or several provisions of this agreement turn out to be invalid, the remained of this agreement remains valid. In this case, the parties will strive to come to an agreement to their original intentions.

________________________________				_______________________________

(For & on behalf of the Principal)					(For & on behalf of the Bidder/ Contractor)

Office Seal							Office Seal

Place…………………………

Date ………………………...

Witness 1:

(Name & Address) :	_______________________________

______________________________

Witness 2:

(Name & Address):	_______________________________

______________________________

Annexure-‘D’

PRICE SCHEDULE FOR GOODS BEING OFFERED FROM ABROAD

Name of the Bidder _________________________				Tender No._____________________________

| 1 | 2 | 3 | 4 | 5 | 6 |  | 7 |  | 8 |  | 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sl No | Item Description | Country of origin | Unit | Qty | Unit Price |  | Total price (5x6) |  | Charges for Insurance & transportation to port/ place of destination |  | Total Price (7+8) |
|  |  |  |  |  | FOB (named port of shipment) | FCA (named place of delivery) | FOB (named port of shipment) | FCA (named place of delivery) | Ocean | Air | CIF |

Total Bid price in foreign Currency ____________________________________________________ _________________ in words.

Quote for AMC and CMC for 05 (Five) years from the elapse of two years warranty period:

| MODEL - | Cost of AMC | Cost of CMC |
| --- | --- | --- |
| 1st yr |  |  |
| 2nd yr |  |  |
| 3rd yr |  |  |
| 4th yr |  |  |
| 5th yr |  |  |

Signature of Bidder

Name:

Business Address:

Note:

- Indian agents name & address ____________________

- Installation, commissioning & training charges, if any_____________________

- Cost of Spares _______________________________

- The Indian agent’s commission shall paid in Indian Rupees only based on the Exchange Rate prevailing on the date of negotiation of documents in accordance with clause 22.1 of GCC.

- The cost of optional items shall be indicated separately.

Annexure-‘E’

PRICE SCHEDULE FOR GOODS BEING OFFERED FROM INDIA

Name of the Bidder _________________________				Tender No._____________________________

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sl. No. | Item Description | Country of Origin | Unit | Qty | Ex-Works. Ex-Warehouse, Ex-show room off the shelf price (inclusive of all taxes already paid) | Total price Ex-Works. Ex-Warehouse, Ex-show room off the shelf price (inclusive of all taxes already paid) 5x6 | VAT & other taxes like excise duty payable, if contract is awarded | Packing & forwarding up to station of dispatch, if any | Charges of inland transportation, insurance up to Lab./Instt. | Installation, Commissioning & training charges, If any. |

Total Bid price in Indian Rupees ____________________________________________________ _________________ in words.

Quote for AMC and CMC for 05 (Five) years from the elapse of two years warranty period:

| MODEL - | Cost of AMC | Cost of CMC |
| --- | --- | --- |
| 1st yr |  |  |
| 2nd yr |  |  |
| 3rd yr |  |  |
| 4th yr |  |  |
| 5th yr |  |  |

Signature of Bidder

Name:

Business Address:

Note:

- The cost of optional items shall be indicated separately.

- Cost of spares ___________________________

Annexure-‘F’

MANUFACUTRER’S AUTHORIZATION FORM

[The Bidder shall require the Manufacturer to fill in this Form in accordance with the instructions indicated. This letter of authorization should be on the letterhead of the Manufacturer and should be signed by a person with the proper authority to sign documents that re binding on the Manufacturer]

Date: [Insert date (as Day, month and year) of Bid submission]

Tender No.: [Insert number from Invitation for Bids]

To: [Insert complete name and address of Purchaser]

WHEREAS

We [insert completer name of Manufacturer], who are official manufacturers of [Insert type of goods manufactured] having factories at [insert full address of Manufacturer’s factories], do hereby authorize [insert complete name of Bidder] to submit a bid the purpose of which is to provide the following goods, manufactured by us [insert name and or brief description of the goods], and to subsequently negotiate and sign the contract.

We hereby extend our full guarantee and warranty in accordance with Clause 20 of the Terms and Conditions of Contract with respect to the Goods offered by the above firm.

Signed: [insert signature(s) of authorized representative(s) of the Manufacturer]

Name: [insert complete name(s) of authorized representative(s) of the Manufacturer]

Title: [insert title]

Duly authorized to sign this Authorization on behalf of: [insert complete name of Bidder]

Dated on  _________________________ day of ________________ [insert date of signing]

Annexure-‘G’

PREVIOUS SUPPLY ORDERS FORMAT

Name of the Firm _______________________________________________________

| Order placed by {Full address of Purchaser] | Order No. and Date | Description and quantity of ordered equipment | Value of order | Date of completion of delivery as per contract | Date of actual completion of delivery | Remarks indicating reasons for late delivery, if any and justification for price difference of their supply order & those quoted to us. | Has the equipment been installed satisfactorily? (Attach a certificate from the Purchaser/ Consigner] | Contact Person along with Telephone no., Fax no. and e-mail address. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Signature and Seal of the Manufacturer/ bidder …………………………………

Place:

Date:

Annexure-‘H’

BIDDER  INFORMATION FORM

[The Bidder shall fill in this form in accordance with the instructions indicated below. No alterations to its format shall be permitted and no substitutions shall be accepted. This should be done on the letter head of the firm]

Date: [Insert date (as day, month and year) of Bid Submission]

Tender No.: [Insert number from invitation of bids]

Page 1 of  ___________ pages

            - Bidder’s Legal Name [Insert Bidder’s legal name]

            - In case of JV, legal name of each party: [insert legal name of each [arty in JV]

            - Bidders actual or intended Country of Registration : [insert actual or intended country of registration]

            - Bidder’s year of registration: [insert Bidder’s year of registration]

            - Bidder’s Legal Address in Country of Registration: [insert bidder’s legal address in country of registration]

            - Bidder’s Authorization Representative Information

Name: [insert Authorization Representative’s name]

Address: [insert Authorization Representative’s address]

Telephone/Fax numbers: [insert Authorization Representative’s telephone/fax numbers]

Email address: [insert Authorization Representative’s email address]

            - Attach are copies of original documents of : [check the box(es) of the attached original documents]

Articles of Incorporation or Registration of firm names in 1 above.